## 版本
“WiseMDC V2.0-北向接口协议”修订记录
版本 | 修订人 | 时间 | 变更内容简述
V2.0 | 科华 | 2020-07-15 | 初稿
*

## outline
version | V1.00.00
summary | Kehua wiseway V3.0 northbound SNMP interface specification is used to realize the consistency of the external interface of the monitoring system. The specification includes two parts of interfaces: 1. Kehua private network adapter v2.0 protocol interface: it includes rfc1628 MIB + Kehua private MIB node, monitors the basic information of SNMP card, real-time data of UPS, temperature and humidity, ordinary air conditioning and other equipment, rated information, current alarm, and supports trap to report common alarm information 2. MIB protocol interface is added to Kehua private network adapter V3.0: monitor the basic information of SNMP card, real-time data, real-time status, alarm information, rating information of UPS, HVDC, battery pack, temperature and humidity and other equipment.
SNMP MIB structure | KEHUA-WiseWay_V3.0.mib
function specification | 1. The interface shall support SNMP V1, V2 and V3 versions. V2 version is used by default. 2. SNMP trap shall be in the form of information request (unless otherwise specified). 3. The SNMP port is 161, the trap port is 162, and the read / write community is public / private respectively. 4. All SNMP table nodes are single index. The SNMP oid and index columns should be arranged in order from small to large. Disorder and line skipping are not allowed. 5. Except for the index field, the data types of all other measuring points are unified as string type. 6. For the SNMP protocol part, the oid value is not allowed to appear in Chinese, but only in English. 7. Open the north interface after all measuring point data are collected with valid data, so as to avoid invalid data obtained by the upper system. 8. Refer to "special value definition" for the value definitions of unsupported measuring points, initial values of measuring points, communication interruption and other special cases. 9. The accuracy of data is rounded when intercepting. 10. For table objects, redundant rows are not allowed (such as rows with racklabel as reserved and backup). 11. When requesting an oid without analog quantity or status quantity, return - 99998. 12. When requesting the oid of a nonexistent or unassigned string, null value is returned
Special value definition | 1) - 99998: invalid values reported by analog quantity and status quantity when the device does not support or communication is abnormal
enclosure | Kehua enterprise private MIB prefix is：.1.3.6.1.4.1.44782.1
...

## Relevant agreement
| Textual conventions | SYNTAX INTEGER | 说明
Grammatical conventions | AlarmLevel | information(1) | System prompt.
|  | warning(2) | Alarm that does not affect the existing business but may affect the business if it develops, and measures can be taken as needed.
|  | minor(3) | It does not affect the existing business, but needs to be overhauled to prevent deteriorating alarms.
|  | major(4) | Alarms that affect business and require immediate troubleshooting.
|  | critical(5) | An alarm that interrupts the service and requires immediate troubleshooting.
| Device Type | UPS(4) | UPS
|  | HVDC(5) | High voltage DC
|  | BMS(7) | Battery pack
|  | airConditionerNormal(11) | Ordinary air conditioner
|  | coulometer(12) | Electricity meter
|  | TH(17) | Temperature and humidity
|  | PDCswitch(19) | Distribution switch
|  | SwitchModule(20) | Switching value module

## Network AdapterV2.0.mib
Equipment type | Name of measuring point | OID | value type | read-write permission | Number of digits after decimal point | unit | Value enumeration | remarks
system | sysDescr | .1.3.6.1.2.1.1.1 | string | r | -
| sysObjectID | .1.3.6.1.2.1.1.2 | OID | r | -
| sysUptime | .1.3.6.1.2.1.1.3 | timeTicks | r | -
| sysContact | .1.3.6.1.2.1.1.4 | string | r | -
| sysName | .1.3.6.1.2.1.1.5 | string | r | -
| sysLocation | .1.3.6.1.2.1.1.6 | string | r | -
UPS | the upsIdent group | [6 empty] | RFC1628 MIB
| upsIdentManufacturer | .1.3.6.1.2.1.33.1.1.1.0 | string | r | -
| upsIdentModel | .1.3.6.1.2.1.33.1.1.2.0 | string | r | -
| upsIdentUPSSoftwareVersion | .1.3.6.1.2.1.33.1.1.3.0 | unsigned integer | r | -
| upsIdentAgentSoftwareVersion | .1.3.6.1.2.1.33.1.1.4.0 | string | r | -
| upsIdentName | .1.3.6.1.2.1.33.1.1.5.0 | string | r | -
| upsIdentAttachedDevices | .1.3.6.1.2.1.33.1.1.6.0 | string | r | -
the upsBattery group
| upsBatteryStatus | .1.3.6.1.2.1.33.1.2.1.0 | unsigned integer | r | 0 |  | unknown(1)， batteryNormal(2)， batteryLow(3)， batteryDepleted(4)
| upsSecondsOnBattery | .1.3.6.1.2.1.33.1.2.2.0 | unsigned integer | r | 0 | s | support or not depend on defferent UPS model
| upsEstimatedMinutesRemaining | .1.3.6.1.2.1.33.1.2.3.0 | unsigned integer | r | 0 | s
| upsEstimatedChargeRemaining | .1.3.6.1.2.1.33.1.2.4.0 | unsigned integer | r | 0 | s
| upsBatteryVoltage | .1.3.6.1.2.1.33.1.2.5.0 | unsigned integer | r | 1 | V
| upsBatteryCurrent | .1.3.6.1.2.1.33.1.2.6.0 | integer | r | 1 | A
| upsBatteryTemperature | .1.3.6.1.2.1.33.1.2.7.0 | integer | r | 0 | ℃
the upsInput group
| upsInputLineBads | .1.3.6.1.2.1.33.1.3.1.0 | unsigned integer | r | 0 |  | input fault times
| upsInputNumLines | .1.3.6.1.2.1.33.1.3.2.0 | unsigned integer | r | 0 |  | support or not depend on defferent UPS model
| upsInputLineIndex | .1.3.6.1.2.1.33.1.3.3.1.1.1 | unsigned integer | r | 0
| upsInputFrequency | .1.3.6.1.2.1.33.1.3.3.1.2.1 | unsigned integer | r | 1 | Hz
| upsInputVoltage | .1.3.6.1.2.1.33.1.3.3.1.3.1 | unsigned integer | r | 0 | V
| upsInputCurrent | .1.3.6.1.2.1.33.1.3.3.1.4.1 | unsigned integer | r | 1 | A
| upsInputTruePower | .1.3.6.1.2.1.33.1.3.3.1.5.1 | unsigned integer | r | 0 | W
| upsInputLineIndex | .1.3.6.1.2.1.33.1.3.3.1.1.2 | unsigned integer | r | 0
| upsInputFrequency | .1.3.6.1.2.1.33.1.3.3.1.2.2 | unsigned integer | r | 1 | Hz
| upsInputVoltage | .1.3.6.1.2.1.33.1.3.3.1.3.2 | unsigned integer | r | 0 | V
| upsInputCurrent | .1.3.6.1.2.1.33.1.3.3.1.4.2 | unsigned integer | r | 1 | A
| upsInputTruePower | .1.3.6.1.2.1.33.1.3.3.1.5.2 | unsigned integer | r | 0 | W
| upsInputLineIndex | .1.3.6.1.2.1.33.1.3.3.1.1.3 | unsigned integer | r | 0
| upsInputFrequency | .1.3.6.1.2.1.33.1.3.3.1.2.3 | unsigned integer | r | 1 | Hz
| upsInputVoltage | .1.3.6.1.2.1.33.1.3.3.1.3.3 | unsigned integer | r | 0 | V
| upsInputCurrent | .1.3.6.1.2.1.33.1.3.3.1.4.3 | unsigned integer | r | 1 | A
| upsInputTruePower | .1.3.6.1.2.1.33.1.3.3.1.5.3 | unsigned integer | r | 0 | W
the upsOutput group
| upsOutputSource | .1.3.6.1.2.1.33.1.4.1.0 | unsigned integer | r | 0 |  | other(1)，none(2)，normal(3)，bypass(4)，battery(5)，booster(6)，reducer(7)
| upsOutputFrequency | .1.3.6.1.2.1.33.1.4.2.0 | unsigned integer | r | 1 | Hz | support or not depend on defferent UPS model
| upsOutputNumLines | .1.3.6.1.2.1.33.1.4.3.0 | unsigned integer | r | 0
| upsOutputLineIndex | .1.3.6.1.2.1.33.1.4.4.1.1.1 | unsigned integer | r | 0
| upsOutputVoltage | .1.3.6.1.2.1.33.1.4.4.1.2.1 | unsigned integer | r | 0 | V
| upsOutputCurrent | .1.3.6.1.2.1.33.1.4.4.1.3.1 | unsigned integer | r | 1 | A
| upsOutputPower | .1.3.6.1.2.1.33.1.4.4.1.4.1 | unsigned integer | r | 0 | W
| upsOutputPercentLoad | .1.3.6.1.2.1.33.1.4.4.1.5.1 | unsigned integer | r | 0 | %
| upsOutputLineIndex | .1.3.6.1.2.1.33.1.4.4.1.1.2 | unsigned integer | r | 0
| upsOutputVoltage | .1.3.6.1.2.1.33.1.4.4.1.2.2 | unsigned integer | r | 0 | V
| upsOutputCurrent | .1.3.6.1.2.1.33.1.4.4.1.3.2 | unsigned integer | r | 1 | A
| upsOutputPower | .1.3.6.1.2.1.33.1.4.4.1.4.2 | unsigned integer | r | 0 | W
| upsOutputPercentLoad | .1.3.6.1.2.1.33.1.4.4.1.5.2 | unsigned integer | r | 0 | %
| upsOutputLineIndex | .1.3.6.1.2.1.33.1.4.4.1.1.3 | unsigned integer | r | 0
| upsOutputVoltage | .1.3.6.1.2.1.33.1.4.4.1.2.3 | unsigned integer | r | 0 | V
| upsOutputCurrent | .1.3.6.1.2.1.33.1.4.4.1.3.3 | unsigned integer | r | 1 | A
| upsOutputPower | .1.3.6.1.2.1.33.1.4.4.1.4.3 | unsigned integer | r | 0 | W
| upsOutputPercentLoad | .1.3.6.1.2.1.33.1.4.4.1.5.3 | unsigned integer | r | 0 | %
the upsBypass group
| upsBypassFrequency | .1.3.6.1.2.1.33.1.5.1.0 | unsigned integer | r | 1 | Hz | support or not depend on defferent UPS model
| upsBypassNumLines | .1.3.6.1.2.1.33.1.5.2.0 | unsigned integer | r | 0
| upsBypassLineIndex | .1.3.6.1.2.1.33.1.5.3.1.1.1 | unsigned integer | r | 0
| upsBypassVoltage | .1.3.6.1.2.1.33.1.5.3.1.2.1 | unsigned integer | r | 0 | V
| upsBypassCurrent | .1.3.6.1.2.1.33.1.5.3.1.3.1 | unsigned integer | r | 1 | A
| upsBypassPower | .1.3.6.1.2.1.33.1.5.3.1.4.1 | unsigned integer | r | 0 | W
| upsBypassLineIndex | .1.3.6.1.2.1.33.1.5.3.1.1.2 | unsigned integer | r | 0
| upsBypassVoltage | .1.3.6.1.2.1.33.1.5.3.1.2.2 | unsigned integer | r | 0 | V
| upsBypassCurrent | .1.3.6.1.2.1.33.1.5.3.1.3.2 | unsigned integer | r | 1 | A
| upsBypassPower | .1.3.6.1.2.1.33.1.5.3.1.4.2 | unsigned integer | r | 0 | W
| upsBypassLineIndex | .1.3.6.1.2.1.33.1.5.3.1.1.3 | unsigned integer | r | 0
| upsBypassVoltage | .1.3.6.1.2.1.33.1.5.3.1.2.3 | unsigned integer | r | 0 | V
| upsBypassCurrent | .1.3.6.1.2.1.33.1.5.3.1.3.3 | unsigned integer | r | 1 | A
| upsBypassPower | .1.3.6.1.2.1.33.1.5.3.1.4.3 | unsigned integer | r | 0 | W
the upsAlarm group
| upsAlarmsPresent | .1.3.6.1.2.1.33.1.6.1.0 | unsigned integer | r | 0 |  | support
| upsAlarmId | .1.3.6.1.2.1.33.1.6.2.1.1 | string | r | - |  | support
| upsAlarmDescr | .1.3.6.1.2.1.33.1.6.2.1.2 | string | r | - |  | support
| upsAlarmTime | .1.3.6.1.2.1.33.1.6.2.1.3 | timestamp | r | 0 |  | support
wellknow trap
| upsAlarmBatteryBad | .1.3.6.1.2.1.33.1.6.3.1 |  | trap |  |  | support or not depend on defferent UPS model
| upsAlarmOnBattery | .1.3.6.1.2.1.33.1.6.3.2 |  | trap
| upsAlarmLowBattery | .1.3.6.1.2.1.33.1.6.3.3 |  | trap
| upsAlarmDepletedBattery | .1.3.6.1.2.1.33.1.6.3.4 |  | trap
| upsAlarmTempBad | .1.3.6.1.2.1.33.1.6.3.5 |  | trap
| upsAlarmInputBad | .1.3.6.1.2.1.33.1.6.3.6 |  | trap
| upsAlarmOutputBad | .1.3.6.1.2.1.33.1.6.3.7 |  | trap
| upsAlarmOutputOverload | .1.3.6.1.2.1.33.1.6.3.8 |  | trap
| upsAlarmOnBypass | .1.3.6.1.2.1.33.1.6.3.9 |  | trap
| upsAlarmBypassBad | .1.3.6.1.2.1.33.1.6.3.10 |  | trap
| upsAlarmOutputOffAsRequested | .1.3.6.1.2.1.33.1.6.3.11 |  | trap
| upsAlarmUpsOffAsRequested | .1.3.6.1.2.1.33.1.6.3.12 |  | trap
| upsAlarmChargerFailed | .1.3.6.1.2.1.33.1.6.3.13 |  | trap
| upsAlarmUpsOutputOff | .1.3.6.1.2.1.33.1.6.3.14 |  | trap
| upsAlarmUpsSystemOff | .1.3.6.1.2.1.33.1.6.3.15 |  | trap
| upsAlarmFanFailure | .1.3.6.1.2.1.33.1.6.3.16 |  | trap
| upsAlarmFuseFailure | .1.3.6.1.2.1.33.1.6.3.17 |  | trap
| upsAlarmGeneralFault | .1.3.6.1.2.1.33.1.6.3.18 |  | trap
| upsAlarmDiagnosticTestFailed | .1.3.6.1.2.1.33.1.6.3.19 |  | trap
| upsAlarmCommunicationsLost | .1.3.6.1.2.1.33.1.6.3.20 |  | trap
| upsAlarmAwaitingPower | .1.3.6.1.2.1.33.1.6.3.21 |  | trap
| upsAlarmShutdownPending | .1.3.6.1.2.1.33.1.6.3.22 |  | trap
| upsAlarmShutdownImminent | .1.3.6.1.2.1.33.1.6.3.23 |  | trap
| upsAlarmTestInProgress | .1.3.6.1.2.1.33.1.6.3.24 |  | trap
the upsTest group
| upsTestId | .1.3.6.1.2.1.33.1.7.1.0 | unsigned integer | r/w |  |  | supported
| upsTestSpinLock | .1.3.6.1.2.1.33.1.7.2.0 |  |  |  |  | Unsupported
| upsTestResultsSummary | .1.3.6.1.2.1.33.1.7.3.0 |  |  |  |  | Unsupported
| upsTestResultsDetail | .1.3.6.1.2.1.33.1.7.4.0 |  |  |  |  | Unsupported
| upsTestStartTime | .1.3.6.1.2.1.33.1.7.5.0 |  |  |  |  | Unsupported
| upsTestElapsedTime | .1.3.6.1.2.1.33.1.7.6.0 |  |  |  |  | Unsupported
| upsTestNoTestsInitiated | .1.3.6.1.2.1.33.1.7.7.1 |  |  |  |  | Unsupported
| upsTestAbortTestInProgress | .1.3.6.1.2.1.33.1.7.7.2 |  | w |  |  | support
| upsTestGeneralSystemsTest | .1.3.6.1.2.1.33.1.7.7.3 |  | w |  |  | support
| upsTestQuickBatteryTest | .1.3.6.1.2.1.33.1.7.7.4 |  |  |  |  | Unsupported
| upsTestDeepBatteryCalibration | .1.3.6.1.2.1.33.1.7.7.5 |  | w |  |  | support
the upsControl group
| upsShutdownType | .1.3.6.1.2.1.33.1.8.1.0 |  |  |  |  | Unsupported
| upsShutdownAfterDelay | .1.3.6.1.2.1.33.1.8.2.0 |  | w |  |  | support
| upsStartupAfterDelay | .1.3.6.1.2.1.33.1.8.3.0 |  | w |  |  | support
| upsRebootWithDuration | .1.3.6.1.2.1.33.1.8.4.0 |  |  |  |  | Unsupported
| upsAutoRestart | .1.3.6.1.2.1.33.1.8.5.0 |  |  |  |  | Unsupported
the upsConfig group
| upsConfigInputVoltage | .1.3.6.1.2.1.33.1.9.1.0 | unsigned integer | r | 0 | V | support
| upsConfigInputFreq | .1.3.6.1.2.1.33.1.9.2.0 | unsigned integer | r | 1 | Hz | support
| upsConfigOutputVoltage | .1.3.6.1.2.1.33.1.9.3.0 | unsigned integer | r | 0 | V | support
| upsConfigOutputFreq | .1.3.6.1.2.1.33.1.9.4.0 | unsigned integer | r | 1 | Hz | support
| upsConfigOutputVA | .1.3.6.1.2.1.33.1.9.5.0 | unsigned integer | r | 0 | VA | support
| upsConfigOutputPower | .1.3.6.1.2.1.33.1.9.6.0 | unsigned integer | r | 0 | W | support
| upsConfigLowBattTime | .1.3.6.1.2.1.33.1.9.7.0 |  |  |  |  | Unsupported
| upsConfigAudibleStatus | .1.3.6.1.2.1.33.1.9.8.0 | unsigned integer | r | 0 |  | 支持
| upsConfigLowVoltageTransferPoint | .1.3.6.1.2.1.33.1.9.9.0 |  |  |  |  | Unsupported
| upsConfigHighVoltageTransferPoint | .1.3.6.1.2.1.33.1.9.10.0 |  |  |  |  | Unsupported
Temperature and humidity module | the thsModuleOne group | [6 empty] | Kehua enterprise private MIB
| th1Name | 1.3.6.1.4.1.44782.1.2.1.1 | string | r |  |  | Support model：KC501B/KC501C/KC501S/KC502
| switch1Name | 1.3.6.1.4.1.44782.1.2.1.2 | string | r
| switch2Name | 1.3.6.1.4.1.44782.1.2.1.3 | string | r
| thsOneTempData | 1.3.6.1.4.1.44782.1.2.1.4.1 | unsigned integer | r | 1 | ℃
| thsOneHumiData | 1.3.6.1.4.1.44782.1.2.1.4.2 | unsigned integer | r | 1 | %
| thsOneAddress | 1.3.6.1.4.1.44782.1.2.1.4.3 | unsigned integer | r | 0
| thsOneCommunication | 1.3.6.1.4.1.44782.1.2.1.5.1 | unsigned integer | r | 0
| thsOneOverTemp | 1.3.6.1.4.1.44782.1.2.1.5.2 | unsigned integer | r | 0
| thsOneUnderTemp | 1.3.6.1.4.1.44782.1.2.1.5.3 | unsigned integer | r | 0
| thsOneOverHumi | 1.3.6.1.4.1.44782.1.2.1.5.4 | unsigned integer | r | 0
| thsOneUnderHumi | 1.3.6.1.4.1.44782.1.2.1.5.5 | unsigned integer | r | 0
| thsOneSwitch1 | 1.3.6.1.4.1.44782.1.2.1.5.6 | unsigned integer | r | 0
| thsOneSwitch2 | 1.3.6.1.4.1.44782.1.2.1.5.7 | unsigned integer | r | 0
| thsOneTempHiConfig | 1.3.6.1.4.1.44782.1.2.1.6.1 | unsigned integer | r/w | 1 | ℃
| thsOneTempLoConfig | 1.3.6.1.4.1.44782.1.2.1.6.2 | unsigned integer | r/w | 1 | ℃
| thsOneHumiHiConfig | 1.3.6.1.4.1.44782.1.2.1.6.3 | unsigned integer | r/w | 1 | %
| thsOneHumiLoConfig | 1.3.6.1.4.1.44782.1.2.1.6.4 | unsigned integer | r/w | 1 | %
| thsOneSwitch1Config | 1.3.6.1.4.1.44782.1.2.1.6.5 | unsigned integer | r/w | 0
| thsOneSwitch2Config | 1.3.6.1.4.1.44782.1.2.1.6.6 | unsigned integer | r/w | 0
the thsModuleTwo group
| th2Name | 1.3.6.1.4.1.44782.1.2.2.1 | string | r | - |  | Support model：KC501B/KC501C/KC501S
| switch3Name | 1.3.6.1.4.1.44782.1.2.2.2 | string | r | -
| switch4Name | 1.3.6.1.4.1.44782.1.2.2.3 | string | r | -
| thsTwoTempData | 1.3.6.1.4.1.44782.1.2.2.4.1 | unsigned integer | r | 1 | ℃
| thsTwoHumiData | 1.3.6.1.4.1.44782.1.2.2.4.2 | unsigned integer | r | 1 | %
| thsTwoAddress | 1.3.6.1.4.1.44782.1.2.2.4.3 | unsigned integer | r | 0
| thsTwoCommunication | 1.3.6.1.4.1.44782.1.2.2.5.1 | unsigned integer | r | 0
| thsTwoOverTemp | 1.3.6.1.4.1.44782.1.2.2.5.2 | unsigned integer | r | 0
| thsTwoUnderTemp | 1.3.6.1.4.1.44782.1.2.2.5.3 | unsigned integer | r | 0
| thsTwoOverHumi | 1.3.6.1.4.1.44782.1.2.2.5.4 | unsigned integer | r | 0
| thsTwoUnderHumi | 1.3.6.1.4.1.44782.1.2.2.5.5 | unsigned integer | r | 0
| thsTwoSwitch1 | 1.3.6.1.4.1.44782.1.2.2.5.6 | unsigned integer | r | 0
| thsTwoSwitch2 | 1.3.6.1.4.1.44782.1.2.2.5.7 | unsigned integer | r | 0
| thsTwoTempHiConfig | 1.3.6.1.4.1.44782.1.2.2.6.1 | unsigned integer | r/w | 1 | ℃
| thsTwoTempLoConfig | 1.3.6.1.4.1.44782.1.2.2.6.2 | unsigned integer | r/w | 1 | ℃
| thsTwoHumiHiConfig | 1.3.6.1.4.1.44782.1.2.2.6.3 | unsigned integer | r/w | 1 | %
| thsTwoHumiLoConfig | 1.3.6.1.4.1.44782.1.2.2.6.4 | unsigned integer | r/w | 1 | %
| thsTwoSwitch1Config | 1.3.6.1.4.1.44782.1.2.2.6.5 | unsigned integer | r/w | 0
| thsTwoSwitch2Config | 1.3.6.1.4.1.44782.1.2.2.6.6 | unsigned integer | r/w | 0
the thsModuleThree group
| th3Name | 1.3.6.1.4.1.44782.1.2.3.1 | string | r | - |  | Reserved
| switch5Name | 1.3.6.1.4.1.44782.1.2.3.2 | string | r | -
| switch6Name | 1.3.6.1.4.1.44782.1.2.3.3 | string | r | -
| thsThreeTempData | 1.3.6.1.4.1.44782.1.2.3.4.1 | unsigned integer | r | 1 | ℃
| thsThreeHumiData | 1.3.6.1.4.1.44782.1.2.3.4.2 | unsigned integer | r | 1 | %
| thsThreeAddress | 1.3.6.1.4.1.44782.1.2.3.4.3 | unsigned integer | r | 0
| thsThreeCommunication | 1.3.6.1.4.1.44782.1.2.3.5.1 | unsigned integer | r | 0
| thsThreeOverTemp | 1.3.6.1.4.1.44782.1.2.3.5.2 | unsigned integer | r | 0
| thsThreeUnderTemp | 1.3.6.1.4.1.44782.1.2.3.5.3 | unsigned integer | r | 0
| thsThreeOverHumi | 1.3.6.1.4.1.44782.1.2.3.5.4 | unsigned integer | r | 0
| thsThreeUnderHumi | 1.3.6.1.4.1.44782.1.2.3.5.5 | unsigned integer | r | 0
| thsThreeSwitch1 | 1.3.6.1.4.1.44782.1.2.3.5.6 | unsigned integer | r | 0
| thsThreeSwitch2 | 1.3.6.1.4.1.44782.1.2.3.5.7 | unsigned integer | r | 0
| thsThreeTempHiConfig | 1.3.6.1.4.1.44782.1.2.3.6.1 | unsigned integer | r/w | 1 | ℃
| thsThreeTempLoConfig | 1.3.6.1.4.1.44782.1.2.3.6.2 | unsigned integer | r/w | 1 | ℃
| thsThreeHumiHiConfig | 1.3.6.1.4.1.44782.1.2.3.6.3 | unsigned integer | r/w | 1 | %
| thsThreeHumiLoConfig | 1.3.6.1.4.1.44782.1.2.3.6.4 | unsigned integer | r/w | 1 | %
| thsThreeSwitch1Config | 1.3.6.1.4.1.44782.1.2.3.6.5 | unsigned integer | r/w | 0
| thsThreeSwitch2Config | 1.3.6.1.4.1.44782.1.2.3.6.6 | unsigned integer | r/w | 0
the thsModuleFour group
| th4Name | 1.3.6.1.4.1.44782.1.2.4.1 | string | r | - |  | Reserved
| switch7Name | 1.3.6.1.4.1.44782.1.2.4.2 | string | r | -
| switch8Name | 1.3.6.1.4.1.44782.1.2.4.3 | string | r | -
| thsFourTempData | 1.3.6.1.4.1.44782.1.2.4.4.1 | unsigned integer | r | 1 | ℃
| thsFourHumiData | 1.3.6.1.4.1.44782.1.2.4.4.2 | unsigned integer | r | 1 | %
| thsFourAddress | 1.3.6.1.4.1.44782.1.2.4.4.3 | unsigned integer | r | 0
| thsFourCommunication | 1.3.6.1.4.1.44782.1.2.4.5.1 | unsigned integer | r | 0
| thsFourOverTemp | 1.3.6.1.4.1.44782.1.2.4.5.2 | unsigned integer | r | 0
| thsFourUnderTemp | 1.3.6.1.4.1.44782.1.2.4.5.3 | unsigned integer | r | 0
| thsFourOverHumi | 1.3.6.1.4.1.44782.1.2.4.5.4 | unsigned integer | r | 0
| thsFourUnderHumi | 1.3.6.1.4.1.44782.1.2.4.5.5 | unsigned integer | r | 0
| thsFourSwitch1 | 1.3.6.1.4.1.44782.1.2.4.5.6 | unsigned integer | r | 0
| thsFourSwitch2 | 1.3.6.1.4.1.44782.1.2.4.5.7 | unsigned integer | r | 0
| thsFourTempHiConfig | 1.3.6.1.4.1.44782.1.2.4.6.1 | unsigned integer | r/w | 1 | ℃
| thsFourTempLoConfig | 1.3.6.1.4.1.44782.1.2.4.6.2 | unsigned integer | r/w | 1 | ℃
| thsFourHumiHiConfig | 1.3.6.1.4.1.44782.1.2.4.6.3 | unsigned integer | r/w | 1 | %
| thsFourHumiLoConfig | 1.3.6.1.4.1.44782.1.2.4.6.4 | unsigned integer | r/w | 1 | %
| thsFourSwitch1Config | 1.3.6.1.4.1.44782.1.2.4.6.5 | unsigned integer | r/w | 0
| thsFourSwitch2Config | 1.3.6.1.4.1.44782.1.2.4.6.6 | unsigned integer | r/w | 0
Ordinary air conditioner | the ac group
| acName | 1.3.6.1.4.1.44782.1.3.1 | string | r | - |  | support
| acDataIndex | 1.3.6.1.4.1.44782.1.3.2.1.1 |  |  |  |  | Reserved
| acTemp | 1.3.6.1.4.1.44782.1.3.2.1.2 | unsigned integer | r | 0.1 | ℃ | support
| acHumi | 1.3.6.1.4.1.44782.1.3.2.1.3 | unsigned integer | r | 0.1 | % | Reserved
| acPowerState | 1.3.6.1.4.1.44782.1.3.2.1.4 | unsigned integer | r | 1 |  | 0:stop;1:run

## Network AdapterV3.0 added.mib
Equipment type | Name of measuring point | OID | value type | read-write permission | Number of digits after decimal point | unit | Value enumeration | remarks
system | systemName | 1.3.6.1.4.1.44782.1.4.1.1 | string | r | -
| systemLocation | 1.3.6.1.4.1.44782.1.4.1.2 | string | r | -
| systemContact | 1.3.6.1.4.1.44782.1.4.1.3 | string | r | -
| systemContactPhone | 1.3.6.1.4.1.44782.1.4.1.4 | string | r | -
| systemSerialNumber | 1.3.6.1.4.1.44782.1.4.1.5 | string | r | -
| systemMAC | 1.3.6.1.4.1.44782.1.4.1.6 | string | r | -
| systemManufacturer | 1.3.6.1.4.1.44782.1.4.1.7 | string | r | -
UPS | ups1equipmentName | 1.3.6.1.4.1.44782.1.4.4.1.1 | string | r | -
| ups1equipmentManufacturer | 1.3.6.1.4.1.44782.1.4.4.1.2 | string | r | -
| ups1equipmentType | 1.3.6.1.4.1.44782.1.4.4.1.3 | string | r | -
| ups1equipmentModel | 1.3.6.1.4.1.44782.1.4.4.1.4 | string | r | -
| ups1equipmentSerialNumber | 1.3.6.1.4.1.44782.1.4.4.1.5 | string | r | -
| ups1installationTime | 1.3.6.1.4.1.44782.1.4.4.1.6 | string | r | -
| ups1installationPosition | 1.3.6.1.4.1.44782.1.4.4.1.7 | string | r | -
| ups1maintenanceExpirationTime | 1.3.6.1.4.1.44782.1.4.4.1.8 | string | r | -
| ups1batteryInstallationReplacementTime | 1.3.6.1.4.1.44782.1.4.4.1.9 | string | r | -
| ups1nextMaintenanceTimeOfBattery | 1.3.6.1.4.1.44782.1.4.4.1.10 | string | r | -
| ups1ratedPower(Kva) | 1.3.6.1.4.1.44782.1.4.4.1.11 | unsigned integer | r | 0
| ups1ratedCapacityOfBattery | 1.3.6.1.4.1.44782.1.4.4.1.12 | unsigned integer | r | 0
| ups1batteryType | 1.3.6.1.4.1.44782.1.4.4.1.13 | unsigned integer | r | 0
| ups1numberOfBatteries | 1.3.6.1.4.1.44782.1.4.4.1.14 | unsigned integer | r | 0
| ups1numberOfBatteriesInASingleGroup | 1.3.6.1.4.1.44782.1.4.4.1.15 | unsigned integer | r | 0
| ups1batteryStatus | 1.3.6.1.4.1.44782.1.4.4.1.16 | unsigned integer | r | 0 |  | 0: Unknown: 1: normal: 2: battery voltage low: 3: Battery exhausted
| ups1batteryTimeRemaining | 1.3.6.1.4.1.44782.1.4.4.1.17 | unsigned integer | r | 1 | min
| ups1remainingCapacityOfBattery | 1.3.6.1.4.1.44782.1.4.4.1.18 | unsigned integer | r | 1 | %
| ups1batteryVoltage | 1.3.6.1.4.1.44782.1.4.4.1.19 | unsigned integer | r | 1 | V
| ups1batteryChargingAndDischargingCurrent | 1.3.6.1.4.1.44782.1.4.4.1.20 | integer | r | 2 | A
| ups1batteryTemperature | 1.3.6.1.4.1.44782.1.4.4.1.21 | integer | r | 1 | ℃
| ups1inputFaultPhaseNumber | 1.3.6.1.4.1.44782.1.4.4.1.22 | unsigned integer | r | 0
| ups1inputTotalPhaseNumber | 1.3.6.1.4.1.44782.1.4.4.1.23 | unsigned integer | r | 0
| ups1inputUPhaseFrequency | 1.3.6.1.4.1.44782.1.4.4.1.24 | unsigned integer | r | 1 | Hz
| ups1inputVPhaseFrequency | 1.3.6.1.4.1.44782.1.4.4.1.25 | unsigned integer | r | 1 | Hz
| ups1inputWPhaseFrequency | 1.3.6.1.4.1.44782.1.4.4.1.26 | unsigned integer | r | 1 | Hz
| ups1inputUPhaseVoltage | 1.3.6.1.4.1.44782.1.4.4.1.27 | unsigned integer | r | 1 | V
| ups1inputVPhaseVoltage | 1.3.6.1.4.1.44782.1.4.4.1.28 | unsigned integer | r | 1 | V
| ups1inputWPhaseVoltage | 1.3.6.1.4.1.44782.1.4.4.1.29 | unsigned integer | r | 1 | V
| ups1inputUPhaseCurrent | 1.3.6.1.4.1.44782.1.4.4.1.30 | unsigned integer | r | 2 | A
| ups1inputVPhaseCurrent | 1.3.6.1.4.1.44782.1.4.4.1.31 | unsigned integer | r | 2 | A
| ups1inputWPhaseCurrent | 1.3.6.1.4.1.44782.1.4.4.1.32 | unsigned integer | r | 2 | A
| ups1inputUPhaseActivePower | 1.3.6.1.4.1.44782.1.4.4.1.33 | unsigned integer | r | 2 | kW
| ups1inputVPhaseActivePower | 1.3.6.1.4.1.44782.1.4.4.1.34 | unsigned integer | r | 2 | kW
| ups1inputWPhaseActivePower | 1.3.6.1.4.1.44782.1.4.4.1.35 | unsigned integer | r | 2 | kW
| ups1inputUPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.4.1.36 | unsigned integer | r | 2 | kVA
| ups1inputVPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.4.1.37 | unsigned integer | r | 2 | kVA
| ups1inputWPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.4.1.38 | unsigned integer | r | 2 | kVA
| ups1powerSupplyMode | 1.3.6.1.4.1.44782.1.4.4.1.39 | unsigned integer | r | - |  | 1: other, 2: none, 3: normal, 4: bypass, 5: battery, 6: boost, 7: depressurize
| ups1outputFrequency | 1.3.6.1.4.1.44782.1.4.4.1.40 | unsigned integer | r | 1 | Hz
| ups1totalOutputPhases | 1.3.6.1.4.1.44782.1.4.4.1.41 | unsigned integer | r | 0
| ups1outputUPhaseVoltage | 1.3.6.1.4.1.44782.1.4.4.1.42 | unsigned integer | r | 1 | V
| ups1outputVPhaseVoltage | 1.3.6.1.4.1.44782.1.4.4.1.43 | unsigned integer | r | 1 | V
| ups1outputWPhaseVoltage | 1.3.6.1.4.1.44782.1.4.4.1.44 | unsigned integer | r | 1 | V
| ups1outputUPhaseCurrent | 1.3.6.1.4.1.44782.1.4.4.1.45 | unsigned integer | r | 2 | A
| ups1outputVPhaseCurrent | 1.3.6.1.4.1.44782.1.4.4.1.46 | unsigned integer | r | 2 | A
| ups1outputWPhaseCurrent | 1.3.6.1.4.1.44782.1.4.4.1.47 | unsigned integer | r | 2 | A
| ups1outputUPhaseActivePower | 1.3.6.1.4.1.44782.1.4.4.1.48 | unsigned integer | r | 2 | kW
| ups1outputVPhaseActivePower | 1.3.6.1.4.1.44782.1.4.4.1.49 | unsigned integer | r | 2 | kW
| ups1outputWPhaseActivePower | 1.3.6.1.4.1.44782.1.4.4.1.50 | unsigned integer | r | 2 | kW
| ups1outputUPhaseLoadRate | 1.3.6.1.4.1.44782.1.4.4.1.51 | unsigned integer | r | 1 | %
| ups1outputVPhaseLoadRate | 1.3.6.1.4.1.44782.1.4.4.1.52 | unsigned integer | r | 1 | %
| ups1outputWPhaseLoadRate | 1.3.6.1.4.1.44782.1.4.4.1.53 | unsigned integer | r | 1 | %
| ups1outputUPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.4.1.54 | unsigned integer | r | 2 | kVA
| ups1outputVPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.4.1.55 | unsigned integer | r | 2 | kVA
| ups1outputWPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.4.1.56 | unsigned integer | r | 2 | kVA
| ups1bypassFrequency | 1.3.6.1.4.1.44782.1.4.4.1.57 | unsigned integer | r | 1 | Hz
| ups1totalPhaseNumberOfBypass | 1.3.6.1.4.1.44782.1.4.4.1.58 | unsigned integer | r | 0
| ups1bypassUPhaseVoltage | 1.3.6.1.4.1.44782.1.4.4.1.59 | unsigned integer | r | 1 | V
| ups1bypassVPhaseVoltage | 1.3.6.1.4.1.44782.1.4.4.1.60 | unsigned integer | r | 1 | V
| ups1bypassWPhaseVoltage | 1.3.6.1.4.1.44782.1.4.4.1.61 | unsigned integer | r | 1 | V
| ups1bypassUPhaseCurrent | 1.3.6.1.4.1.44782.1.4.4.1.62 | unsigned integer | r | 2 | A
| ups1bypassVPhaseCurrent | 1.3.6.1.4.1.44782.1.4.4.1.63 | unsigned integer | r | 2 | A
| ups1bypassWPhaseCurrent | 1.3.6.1.4.1.44782.1.4.4.1.64 | unsigned integer | r | 2 | A
| ups1bypassUPhaseActivePower | 1.3.6.1.4.1.44782.1.4.4.1.65 | unsigned integer | r | 2 | kW
| ups1bypassVPhaseActivePower | 1.3.6.1.4.1.44782.1.4.4.1.66 | unsigned integer | r | 2 | kW
| ups1bypassWPhaseActivePower | 1.3.6.1.4.1.44782.1.4.4.1.67 | unsigned integer | r | 2 | kW
| ups1bypassUPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.4.1.68 | unsigned integer | r | 2 | kVA
| ups1bypassVPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.4.1.69 | unsigned integer | r | 2 | kVA
| ups1bypassWPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.4.1.70 | unsigned integer | r | 2 | kVA
| ups1abnormalCommunication | 1.3.6.1.4.1.44782.1.4.4.1.71 | unsigned integer | r | -
| ups1batteryAbnormal | 1.3.6.1.4.1.44782.1.4.4.1.72 | unsigned integer | r | -
| ups1batteryPowered | 1.3.6.1.4.1.44782.1.4.4.1.73 | unsigned integer | r | -
| ups1batteryLowVoltage | 1.3.6.1.4.1.44782.1.4.4.1.74 | unsigned integer | r | -
| ups1batteryDamage | 1.3.6.1.4.1.44782.1.4.4.1.75 | unsigned integer | r | -
| ups1temperatureAbnormal | 1.3.6.1.4.1.44782.1.4.4.1.76 | unsigned integer | r | -
| ups1inputAbnormal | 1.3.6.1.4.1.44782.1.4.4.1.77 | unsigned integer | r | -
| ups1outputAbnormal | 1.3.6.1.4.1.44782.1.4.4.1.78 | unsigned integer | r | -
| ups1overLoad | 1.3.6.1.4.1.44782.1.4.4.1.79 | unsigned integer | r | -
| ups1bypassSupply | 1.3.6.1.4.1.44782.1.4.4.1.80 | unsigned integer | r | -
| ups1bypassAbnormal | 1.3.6.1.4.1.44782.1.4.4.1.81 | unsigned integer | r | -
| ups1remoteShutdownOutput | 1.3.6.1.4.1.44782.1.4.4.1.82 | unsigned integer | r | -
| ups1remoteShutdownOfUPS | 1.3.6.1.4.1.44782.1.4.4.1.83 | unsigned integer | r | -
| ups1batteryChargingFailure | 1.3.6.1.4.1.44782.1.4.4.1.84 | unsigned integer | r | -
| ups1upsOutputOff | 1.3.6.1.4.1.44782.1.4.4.1.85 | unsigned integer | r | -
| ups1upsShutdown | 1.3.6.1.4.1.44782.1.4.4.1.86 | unsigned integer | r | -
| ups1fanFailure | 1.3.6.1.4.1.44782.1.4.4.1.87 | unsigned integer | r | -
| ups1theFuseIsBlown | 1.3.6.1.4.1.44782.1.4.4.1.88 | unsigned integer | r | -
| ups1generalFailure | 1.3.6.1.4.1.44782.1.4.4.1.89 | unsigned integer | r | -
| ups1testFailed | 1.3.6.1.4.1.44782.1.4.4.1.90 | unsigned integer | r | -
| ups1delayShutdownOfUPS | 1.3.6.1.4.1.44782.1.4.4.1.91 | unsigned integer | r | -
| ups1shutDownUPSImmediately | 1.3.6.1.4.1.44782.1.4.4.1.92 | unsigned integer | r | -
| ups1testing | 1.3.6.1.4.1.44782.1.4.4.1.93 | unsigned integer | r | -
| ups1batteryOperationStatus | 1.3.6.1.4.1.44782.1.4.4.1.94 | unsigned integer | r | - |  | 0 - discharge; 1 - even charge; 2 - floating charge; 3 - Unknown
| ups1systemOperationMode | 1.3.6.1.4.1.44782.1.4.4.1.95 | unsigned integer | r | - |  | 0: initialization, 1: fault protection, 2: shutdown, 3: parallel shutdown, 4: bypass, 5: inverter, 6: grid connected self aging, 7: Eco mode, 8: frequency conversion mode, 9: maintenance bypass, 10: grid connected self aging shutdown, 11: frequency conversion mode shutdown, 12: self aging bypass output, 13: others
| ups1rectifierWorkingState | 1.3.6.1.4.1.44782.1.4.4.1.96 | unsigned integer | r | - |  | 0 - startup, 1 - fault, 2 - mains boost; 3 - battery boost;
| ups1overTemperatureProtection | 1.3.6.1.4.1.44782.1.4.4.1.97 | unsigned integer | r | -
| ups1inputPhaseAbnormal | 1.3.6.1.4.1.44782.1.4.4.1.98 | unsigned integer | r | -
| ups1bypasstPhaseAbnormal | 1.3.6.1.4.1.44782.1.4.4.1.99 | unsigned integer | r | -
| ups1otherAlarm | 1.3.6.1.4.1.44782.1.4.4.1.100 | unsigned integer | r | -
| ups1assetNumber | 1.3.6.1.4.1.44782.1.4.4.1.101 | string | r | -
| ups1numberOfModules | 1.3.6.1.4.1.44782.1.4.4.1.124 | unsigned integer | r | 0
| ups1moduleTable | 1.3.6.1.4.1.44782.1.4.4.1.125
| ups1moduleEntry | 1.3.6.1.4.1.44782.1.4.4.1.125.1
| ups1moduleIndex | 1.3.6.1.4.1.44782.1.4.4.1.125.1.1 | unsigned integer | r | 0 |  | 0~25
| ups1moduleInputUPhaseVoltage | 1.3.6.1.4.1.44782.1.4.4.1.125.1.2 | unsigned integer | r | 1 | V
| ups1moduleInputVPhaseVoltage | 1.3.6.1.4.1.44782.1.4.4.1.125.1.3 | unsigned integer | r | 1 | V
| ups1moduleInputWPhaseVoltage | 1.3.6.1.4.1.44782.1.4.4.1.125.1.4 | unsigned integer | r | 1 | V
| ups1moduleInputUPhaseCurrent | 1.3.6.1.4.1.44782.1.4.4.1.125.1.5 | unsigned integer | r | 2 | A
| ups1moduleInputVPhaseCurrent | 1.3.6.1.4.1.44782.1.4.4.1.125.1.6 | unsigned integer | r | 2 | A
| ups1moduleInputWPhaseCurrent | 1.3.6.1.4.1.44782.1.4.4.1.125.1.7 | unsigned integer | r | 2 | A
| ups1moduleInputFrequency | 1.3.6.1.4.1.44782.1.4.4.1.125.1.8 | unsigned integer | r | 1 | Hz
| ups1moduleInputUPhaseActivePower | 1.3.6.1.4.1.44782.1.4.4.1.125.1.9 | unsigned integer | r | 2 | kW
| ups1moduleInputVPhaseActivePower | 1.3.6.1.4.1.44782.1.4.4.1.125.1.10 | unsigned integer | r | 2 | kW
| ups1moduleInputWPhaseActivePower | 1.3.6.1.4.1.44782.1.4.4.1.125.1.11 | unsigned integer | r | 2 | kW
| ups1moduleInputUPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.4.1.125.1.12 | unsigned integer | r | 2 | kVA
| ups1moduleInputVPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.4.1.125.1.13 | unsigned integer | r | 2 | kVA
| ups1moduleInputWPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.4.1.125.1.14 | unsigned integer | r | 2 | kVA
| ups1moduleOutputUPhaseVoltage | 1.3.6.1.4.1.44782.1.4.4.1.125.1.15 | unsigned integer | r | 1 | V
| ups1moduleOutputVPhaseVoltage | 1.3.6.1.4.1.44782.1.4.4.1.125.1.16 | unsigned integer | r | 1 | V
| ups1moduleOutputWPhaseVoltage | 1.3.6.1.4.1.44782.1.4.4.1.125.1.17 | unsigned integer | r | 1 | V
| ups1moduleOutputFrequency | 1.3.6.1.4.1.44782.1.4.4.1.125.1.18 | unsigned integer | r | 1 | Hz
| ups1moduleOutputUPhaseCurrent | 1.3.6.1.4.1.44782.1.4.4.1.125.1.19 | unsigned integer | r | 2 | A
| ups1moduleOutputVPhaseCurrent | 1.3.6.1.4.1.44782.1.4.4.1.125.1.20 | unsigned integer | r | 2 | A
| ups1moduleOutputWPhaseCurrent | 1.3.6.1.4.1.44782.1.4.4.1.125.1.21 | unsigned integer | r | 2 | A
| ups1moduleOutputUPhaseActivePower | 1.3.6.1.4.1.44782.1.4.4.1.125.1.22 | unsigned integer | r | 2 | kW
| ups1moduleOutputVPhaseActivePower | 1.3.6.1.4.1.44782.1.4.4.1.125.1.23 | unsigned integer | r | 2 | kW
| ups1moduleOutputWPhaseActivePower | 1.3.6.1.4.1.44782.1.4.4.1.125.1.24 | unsigned integer | r | 2 | kW
| ups1moduleOutputUPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.4.1.125.1.25 | unsigned integer | r | 2 | kVA
| ups1moduleOutputsVPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.4.1.125.1.26 | unsigned integer | r | 2 | kVA
| ups1moduleOutputsWPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.4.1.125.1.27 | unsigned integer | r | 2 | kVA
| ups1moduleOutputUPhaseLoadRate | 1.3.6.1.4.1.44782.1.4.4.1.125.1.28 | unsigned integer | r | 1 | %
| ups1moduleOutputVPhaseLoadRate | 1.3.6.1.4.1.44782.1.4.4.1.125.1.29 | unsigned integer | r | 1 | %
| ups1moduleOutputWPhaseLoadRate | 1.3.6.1.4.1.44782.1.4.4.1.125.1.30 | unsigned integer | r | 1 | %
| ups1moduleAbnormal | 1.3.6.1.4.1.44782.1.4.4.1.125.1.31 | unsigned integer | r | -
| ups1DischargeManage | 1.3.6.1.4.1.44782.1.4.4.1.126
| ups1CancelDischarge | 1.3.6.1.4.1.44782.1.4.4.1.126.1 | unsigned integer | w | -
| ups1DischargeTime | 1.3.6.1.4.1.44782.1.4.4.1.126.2 | unsigned integer | w | -
| ups1DischargeTimeVolt | 1.3.6.1.4.1.44782.1.4.4.1.126.3 | unsigned integer | w | -
| ups1Test | 1.3.6.1.4.1.44782.1.4.4.1.126.4 | unsigned integer | w | -
| ups1DisechargeSetVolt | 1.3.6.1.4.1.44782.1.4.4.1.126.5 | unsigned integer | w | -
| ups1DischargeResult | 1.3.6.1.4.1.44782.1.4.4.1.126.6 | unsigned integer | r | -
HVDC | hvdc1EquipmentName | 1.3.6.1.4.1.44782.1.4.5.1.1 | string | r | -
| hvdc1EquipmentManufacturer | 1.3.6.1.4.1.44782.1.4.5.1.2 | string | r | -
| hvdc1EquipmentType | 1.3.6.1.4.1.44782.1.4.5.1.3 | string | r | -
| hvdc1EquipmentModel | 1.3.6.1.4.1.44782.1.4.5.1.4 | string | r | -
| hvdc1EquipmentSerialNumber | 1.3.6.1.4.1.44782.1.4.5.1.5 | string | r | -
| hvdc1InstallationTime | 1.3.6.1.4.1.44782.1.4.5.1.6 | string | r | -
| hvdc1InstallationPosition | 1.3.6.1.4.1.44782.1.4.5.1.7 | string | r | -
| hvdc1MaintenanceExpirationTime | 1.3.6.1.4.1.44782.1.4.5.1.8 | string | r | -
| hvdc1BatteryInstallationReplacementTime | 1.3.6.1.4.1.44782.1.4.5.1.9 | string | r | -
| hvdc1NextMaintenanceTimeOfBattery | 1.3.6.1.4.1.44782.1.4.5.1.10 | string | r | -
| hvdc1RatedPower | 1.3.6.1.4.1.44782.1.4.5.1.11 | unsigned integer | r | 0 | kVA
| hvdc1RatedCapacityOfBattery | 1.3.6.1.4.1.44782.1.4.5.1.12 | unsigned integer | r | 0 | Ah
| hvdc1BatteryType | 1.3.6.1.4.1.44782.1.4.5.1.13 | unsigned integer | r | 0
| hvdc1NumberOfBatteries | 1.3.6.1.4.1.44782.1.4.5.1.14 | unsigned integer | r | 0
| hvdc1NumberOfBatteriesInASingleGroup | 1.3.6.1.4.1.44782.1.4.5.1.15 | unsigned integer | r | 0
| hvdc1ACInputQuantity | 1.3.6.1.4.1.44782.1.4.5.1.16 | unsigned integer | r | 0
| hvdc1ACOutputQuantity | 1.3.6.1.4.1.44782.1.4.5.1.17 | unsigned integer | r | 0
| hvdc1NumberOfRectifierModules | 1.3.6.1.4.1.44782.1.4.5.1.18 | unsigned integer | r | 0
| hvdc1NumberOfBatteriesD | 1.3.6.1.4.1.44782.1.4.5.1.19 | unsigned integer | r | 0
| hvdc1BusVoltage | 1.3.6.1.4.1.44782.1.4.5.1.20 | unsigned integer | r | 1 | V
| hvdc1BusPositiveVoltage | 1.3.6.1.4.1.44782.1.4.5.1.21 | unsigned integer | r | 1 | V
| hvdc1BusNegativeVoltage | 1.3.6.1.4.1.44782.1.4.5.1.22 | unsigned integer | r | 1 | V
| hvdc1LoadTotalOutputCurrent | 1.3.6.1.4.1.44782.1.4.5.1.23 | unsigned integer | r | 2 | A
| hvdc1TotalOutputPower | 1.3.6.1.4.1.44782.1.4.5.1.24 | unsigned integer | r | 2 | kW
| hvdc1AmbientTemperature | 1.3.6.1.4.1.44782.1.4.5.1.25 | integer | r | 1 | ℃
| hvdc1DCCabinetTemperature | 1.3.6.1.4.1.44782.1.4.5.1.26 | integer | r | 1 | ℃
| hvdc1RectifierCabinet1Temperature | 1.3.6.1.4.1.44782.1.4.5.1.27 | integer | r | 1 | ℃
| hvdc1RectifierCabinet2Temperature | 1.3.6.1.4.1.44782.1.4.5.1.28 | integer | r | 1 | ℃
| hvdc1SystemState | 1.3.6.1.4.1.44782.1.4.5.1.29 | unsigned integer | r | 0
| hvdc1ACInputTable | 1.3.6.1.4.1.44782.1.4.5.1.30
| hvdc1ACInputEntry | 1.3.6.1.4.1.44782.1.4.5.1.30.1
| hvdc1ACInputIndex | 1.3.6.1.4.1.44782.1.4.5.1.30.1.1 | unsigned integer | r | 0 |  | 0~3
| hvdc1ACInputUPhaseVoltage | 1.3.6.1.4.1.44782.1.4.5.1.30.1.2 | unsigned integer | r | 1 | V
| hvdc1ACInputVPhaseVoltage | 1.3.6.1.4.1.44782.1.4.5.1.30.1.3 | unsigned integer | r | 1 | V
| hvdc1ACInputWPhaseVoltage | 1.3.6.1.4.1.44782.1.4.5.1.30.1.4 | unsigned integer | r | 1 | V
| hvdc1ACInputUPhaseCurrent | 1.3.6.1.4.1.44782.1.4.5.1.30.1.5 | unsigned integer | r | 2 | A
| hvdc1ACInputVPhaseCurrent | 1.3.6.1.4.1.44782.1.4.5.1.30.1.6 | unsigned integer | r | 2 | A
| hvdc1ACInputWPhaseCurrent | 1.3.6.1.4.1.44782.1.4.5.1.30.1.7 | unsigned integer | r | 2 | A
| hvdc1ACInputFrequency | 1.3.6.1.4.1.44782.1.4.5.1.30.1.8 | unsigned integer | r | 1 | Hz
| hvdc1ACInputTotalApparentPower | 1.3.6.1.4.1.44782.1.4.5.1.30.1.9 | unsigned integer | r | 2 | kVA
| hvdc1ACInputTotalReactivePower | 1.3.6.1.4.1.44782.1.4.5.1.30.1.10 | unsigned integer | r | 2 | kVar
| hvdc1ACInputTotalActivePower | 1.3.6.1.4.1.44782.1.4.5.1.30.1.11 | unsigned integer | r | 2 | kW
| hvdc1ACInputUPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.5.1.30.1.12 | unsigned integer | r | 2 | kVA
| hvdc1ACInputVPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.5.1.30.1.13 | unsigned integer | r | 2 | kVA
| hvdc1ACInputWPhaseApparentPower | 1.3.6.1.4.1.44782.1.4.5.1.30.1.14 | unsigned integer | r | 2 | kVA
| hvdc1ACInputU-PhaseActivePower | 1.3.6.1.4.1.44782.1.4.5.1.30.1.15 | unsigned integer | r | 2 | kW
| hvdc1ACInputVPhaseActivePower | 1.3.6.1.4.1.44782.1.4.5.1.30.1.16 | unsigned integer | r | 2 | kW
| hvdc1ACInputWPhaseActivePower | 1.3.6.1.4.1.44782.1.4.5.1.30.1.17 | unsigned integer | r | 2 | kW
| hvdc1ACInputU-PhaseReactivePower | 1.3.6.1.4.1.44782.1.4.5.1.30.1.18 | unsigned integer | r | 2 | kVar
| hvdc1ACInputV-PhaseReactivePower | 1.3.6.1.4.1.44782.1.4.5.1.30.1.19 | unsigned integer | r | 2 | kVar
| hvdc1ACInputWPhaseReactivePower | 1.3.6.1.4.1.44782.1.4.5.1.30.1.20 | unsigned integer | r | 2 | kVar
| hvdc1ACInputUPhasePowerFactor | 1.3.6.1.4.1.44782.1.4.5.1.30.1.21 | unsigned integer | r | 2
| hvdc1ACInputVPhasePowerFactor | 1.3.6.1.4.1.44782.1.4.5.1.30.1.22 | unsigned integer | r | 2
| hvdc1ACInputWPhasePowerFactor | 1.3.6.1.4.1.44782.1.4.5.1.30.1.23 | unsigned integer | r | 2
| hvdc1ACInputAlarm | 1.3.6.1.4.1.44782.1.4.5.1.30.1.24 | unsigned integer | r | -
| hvdc1BatteryStatus | 1.3.6.1.4.1.44782.1.4.5.1.31 | unsigned integer | r | 0
| hvdc1DischargeStateBatteryResidualCapacity | 1.3.6.1.4.1.44782.1.4.5.1.32 | unsigned integer | r | 1 | %
| hvdc1DischargeState-ResidualDischargeTime | 1.3.6.1.4.1.44782.1.4.5.1.33 | unsigned integer | r | 1 | Min
| hvdc1TotalBatteryCurrent | 1.3.6.1.4.1.44782.1.4.5.1.34 | integer | r | 2 | A
| hvdc1BatteryPackTable | 1.3.6.1.4.1.44782.1.4.5.1.35
| hvdc1BatteryPackEntry | 1.3.6.1.4.1.44782.1.4.5.1.35.1
| hvdc1BatteryPackIndex | 1.3.6.1.4.1.44782.1.4.5.1.35.1.1 | unsigned integer | r | 0 |  | 0~7
| hvdc1BatteryPackCurrent | 1.3.6.1.4.1.44782.1.4.5.1.35.1.2 | integer | r | 2 | A
| hvdc1BatteryPackTemperature | 1.3.6.1.4.1.44782.1.4.5.1.35.1.3 | integer | r | 1 | ℃
| hvdc1BatteryPackBreaker | 1.3.6.1.4.1.44782.1.4.5.1.35.1.4 | unsigned integer | r | -
| hvdc1BatteryPackOutputPFuse | 1.3.6.1.4.1.44782.1.4.5.1.35.1.5 | unsigned integer | r | -
| hvdc1BatteryPackOutputNFuse | 1.3.6.1.4.1.44782.1.4.5.1.35.1.6 | unsigned integer | r | -
| hvdc1TotalLoadCurrent | 1.3.6.1.4.1.44782.1.4.5.1.36 | unsigned integer | r | 2 | A
| hvdc1DCLightningArrester | 1.3.6.1.4.1.44782.1.4.5.1.37 | unsigned integer | r | -
| hvdc1DCBusBreaker | 1.3.6.1.4.1.44782.1.4.5.1.38 | unsigned integer | r | -
| hvdc1DCBusPInsulationResister | 1.3.6.1.4.1.44782.1.4.5.1.39 | unsigned integer | r | 1 | kΩ
| hvdc1DCBusNInsulationResister | 1.3.6.1.4.1.44782.1.4.5.1.40 | unsigned integer | r | 1 | kΩ
| hvdc1DCBranchTable | 1.3.6.1.4.1.44782.1.4.5.1.41
| hvdc1DCBranchEntry | 1.3.6.1.4.1.44782.1.4.5.1.41.1
| hvdc1DCBranchIndex | 1.3.6.1.4.1.44782.1.4.5.1.41.1.1 | unsigned integer | r | 0 |  | 0~31
| hvdc1DCBranchLoadCurrent | 1.3.6.1.4.1.44782.1.4.5.1.41.1.2 | unsigned integer | r | 2 | A
| hvdc1DCBranchPInsulationResister | 1.3.6.1.4.1.44782.1.4.5.1.41.1.3 | unsigned integer | r | 1 | kΩ
| hvdc1DCBranchNInsulationResister | 1.3.6.1.4.1.44782.1.4.5.1.41.1.4 | unsigned integer | r | 1 | kΩ
| hvdc1DCBranchBreaker | 1.3.6.1.4.1.44782.1.4.5.1.41.1.5 | unsigned integer | r | -
| hvdc1DCBranchOutputPFuse | 1.3.6.1.4.1.44782.1.4.5.1.41.1.6 | unsigned integer | r | -
| hvdc1DCBranchOutputNFuse | 1.3.6.1.4.1.44782.1.4.5.1.41.1.7 | unsigned integer | r | -
| hvdc1RectifierModuleTable | 1.3.6.1.4.1.44782.1.4.5.1.42
| hvdc1RectifierModuleEntry | 1.3.6.1.4.1.44782.1.4.5.1.42.1
| hvdc1RectifierModuleIndex | 1.3.6.1.4.1.44782.1.4.5.1.42.1.1 | unsigned integer | r | 0 |  | 0~25
| hvdc1RectifierModuleVoltage | 1.3.6.1.4.1.44782.1.4.5.1.42.1.2 | unsigned integer | r | 1 | V
| hvdc1RectifierModuleCurrent | 1.3.6.1.4.1.44782.1.4.5.1.42.1.3 | unsigned integer | r | 2 | A
| hvdc1RectifierModulePower | 1.3.6.1.4.1.44782.1.4.5.1.42.1.4 | unsigned integer | r | 2 | kW
| hvdc1RectifierModuleTemperature | 1.3.6.1.4.1.44782.1.4.5.1.42.1.5 | unsigned integer | r | 1 | ℃
| hvdc1RectifierModuleStatus | 1.3.6.1.4.1.44782.1.4.5.1.42.1.6 | unsigned integer | r | -
| hvdc1RectificationModuleAlarm | 1.3.6.1.4.1.44782.1.4.5.1.42.1.7 | unsigned integer | r | -
| hvdc1CommunicationStatus | 1.3.6.1.4.1.44782.1.4.5.1.43 | unsigned integer | r | -
| hvdc1DCTotalOutputAlarm | 1.3.6.1.4.1.44782.1.4.5.1.44 | unsigned integer | r | -
| hvdc1EnvironmentTemperatureAbnormal | 1.3.6.1.4.1.44782.1.4.5.1.45 | unsigned integer | r | -
| hvdc1InternalCommunicationAbnormal | 1.3.6.1.4.1.44782.1.4.5.1.46 | unsigned integer | r | -
| hvdc1BatteryAlarm | 1.3.6.1.4.1.44782.1.4.5.1.47 | unsigned integer | r | -
| hvdc1InsulationAlarm | 1.3.6.1.4.1.44782.1.4.5.1.48 | unsigned integer | r | -
| hvdc1OtherAlarms | 1.3.6.1.4.1.44782.1.4.5.1.49 | unsigned integer | r | -
Battery pack 1 | terminalVoltageOfBatteryPack1 | 1.3.6.1.4.1.44782.1.4.7.1.1 | unsigned integer | r | 1 | V
| chargingAndDischargingCurrentOfBatteryPack1 | 1.3.6.1.4.1.44782.1.4.7.1.2 | integer | r | 2 | A
| remainingCapacityOfBatteryPack1 | 1.3.6.1.4.1.44782.1.4.7.1.3 | unsigned integer | r | 1 | %
| timeRemainingOfBatteryPack1 | 1.3.6.1.4.1.44782.1.4.7.1.4 | unsigned integer | r | 1 | Min
| batteryPack1AmbientTemperature | 1.3.6.1.4.1.44782.1.4.7.1.5 | unsigned integer | r | 1 | ℃
| batteryPack1AmbientHumidity | 1.3.6.1.4.1.44782.1.4.7.1.6 | unsigned integer | r | 1 | %
| batteryPack1BatteryRunningStatus | 1.3.6.1.4.1.44782.1.4.7.1.7 | unsigned integer | r | 0 |  | 0-discharge, 1-equalizing charge, 2-floating charge, 3-unknown
| batteryPack1TerminalVoltageTooHigh | 1.3.6.1.4.1.44782.1.4.7.1.8 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack1TerminalVoltageTooLow | 1.3.6.1.4.1.44782.1.4.7.1.9 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| theChargingCurrentOfBatteryPack1IsTooHigh | 1.3.6.1.4.1.44782.1.4.7.1.10 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| theDischargeCurrentOfBatteryPack1IsTooHigh | 1.3.6.1.4.1.44782.1.4.7.1.11 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| unevenFloatingChargeVoltageOfBatteryPack1 | 1.3.6.1.4.1.44782.1.4.7.1.12 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| unevenDischargeVoltageOfBatteryPack1 | 1.3.6.1.4.1.44782.1.4.7.1.13 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| unevenVoltageOfBatteryPack1 | 1.3.6.1.4.1.44782.1.4.7.1.14 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack1BatteryPackCapacityTooLow | 1.3.6.1.4.1.44782.1.4.7.1.15 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack1AmbientTemperatureTooHigh | 1.3.6.1.4.1.44782.1.4.7.1.16 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack1AmbientTemperatureTooLow | 1.3.6.1.4.1.44782.1.4.7.1.17 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| theAmbientHumidityOfBatteryPack1IsTooHigh | 1.3.6.1.4.1.44782.1.4.7.1.18 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| theAmbientHumidityOfBatteryPack1IsTooLow | 1.3.6.1.4.1.44782.1.4.7.1.19 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| otherFaultsOfBatteryPack1 | 1.3.6.1.4.1.44782.1.4.7.1.20 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| numberOfBatteriesInBatteryPack1 | 1.3.6.1.4.1.44782.1.4.7.1.21 | unsigned integer | r | 0
| batteryPack1BatteryTable | 1.3.6.1.4.1.44782.1.4.7.1.22
| batteryPack1BatteryEntry | 1.3.6.1.4.1.44782.1.4.7.1.22.1
| batteryPack1BatteryIndex | 1.3.6.1.4.1.44782.1.4.7.1.22.1.1 | unsigned integer |  | 0 |  | 1~32
| batteryPack1BatteryVoltage | 1.3.6.1.4.1.44782.1.4.7.1.22.1.2 | unsigned integer | r | 2 | V
| batteryPack1BatteryInternalResistance | 1.3.6.1.4.1.44782.1.4.7.1.22.1.3 | unsigned integer | r | 2 | Ω
| batteryPack1BatteryTemperature | 1.3.6.1.4.1.44782.1.4.7.1.22.1.4 | unsigned integer | r | 1 | ℃
| batteryPack1BatterySOC | 1.3.6.1.4.1.44782.1.4.7.1.22.1.5 | unsigned integer | r | 1 | %
| batteryPack1BatterySOH | 1.3.6.1.4.1.44782.1.4.7.1.22.1.6 | unsigned integer | r | 1 | %
| batteryPerformanceOfBatteryPack1 | 1.3.6.1.4.1.44782.1.4.7.1.22.1.7 | unsigned integer | r | - |  | 0 - the battery runs well; 1 - performance degradation; 2 - it is recommended to replace the battery;
| abnormalCommunicationOfBatteryPack1 | 1.3.6.1.4.1.44782.1.4.7.1.22.1.8 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack1BatteryVoltageTooHigh | 1.3.6.1.4.1.44782.1.4.7.1.22.1.9 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack1BatteryVoltageTooLow | 1.3.6.1.4.1.44782.1.4.7.1.22.1.10 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack1BatteryInternalResistanceTooHigh | 1.3.6.1.4.1.44782.1.4.7.1.22.1.11 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack1BatteryTemperatureTooHigh | 1.3.6.1.4.1.44782.1.4.7.1.22.1.12 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack1BatteryTemperatureTooLow | 1.3.6.1.4.1.44782.1.4.7.1.22.1.13 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack1BatteryCapacityTooLow | 1.3.6.1.4.1.44782.1.4.7.1.22.1.14 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack1BatteryOtherFaults | 1.3.6.1.4.1.44782.1.4.7.1.22.1.15 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
Battery pack 2 | terminalVoltageOfBatteryPack2 | 1.3.6.1.4.1.44782.1.4.7.2.1 | unsigned integer | r | 1 | V
| chargingAndDischargingCurrentOfBatteryPack2 | 1.3.6.1.4.1.44782.1.4.7.2.2 | integer | r | 2 | A
| remainingCapacityOfBatteryPack2 | 1.3.6.1.4.1.44782.1.4.7.2.3 | unsigned integer | r | 1 | %
| batteryPack2TimeRemaining | 1.3.6.1.4.1.44782.1.4.7.2.4 | unsigned integer | r | 1 | Min
| batteryPack2AmbientTemperature | 1.3.6.1.4.1.44782.1.4.7.2.5 | unsigned integer | r | 1 | ℃
| batteryPack2AmbientHumidity | 1.3.6.1.4.1.44782.1.4.7.2.6 | unsigned integer | r | 1 | %
| batteryPack2BatteryRunningStatus | 1.3.6.1.4.1.44782.1.4.7.2.7 | unsigned integer | r | 0 |  | 0-discharge, 1-equalizing charge, 2-floating charge, 3-unknown
| batteryPack2TerminalVoltageTooHigh | 1.3.6.1.4.1.44782.1.4.7.2.8 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack2TerminalVoltageTooLow | 1.3.6.1.4.1.44782.1.4.7.2.9 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| theChargingCurrentOfBatteryPack2IsTooHigh | 1.3.6.1.4.1.44782.1.4.7.2.10 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| theDischargeCurrentOfBatteryPack2IsTooHigh | 1.3.6.1.4.1.44782.1.4.7.2.11 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| unevenFloatingChargeVoltageOfBatteryPack2 | 1.3.6.1.4.1.44782.1.4.7.2.12 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| unevenDischargeVoltageOfBatteryPack2 | 1.3.6.1.4.1.44782.1.4.7.2.13 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| unevenVoltageOfBatteryPack2 | 1.3.6.1.4.1.44782.1.4.7.2.14 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack2BatteryPackCapacityTooLow | 1.3.6.1.4.1.44782.1.4.7.2.15 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack2AmbientTemperatureTooHigh | 1.3.6.1.4.1.44782.1.4.7.2.16 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack2AmbientTemperatureTooLow | 1.3.6.1.4.1.44782.1.4.7.2.17 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| theAmbientHumidityOfBatteryPack2IsTooHigh | 1.3.6.1.4.1.44782.1.4.7.2.18 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack2AmbientHumidityTooLow | 1.3.6.1.4.1.44782.1.4.7.2.19 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| otherFaultsOfBatteryPack2 | 1.3.6.1.4.1.44782.1.4.7.2.20 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| numberOfBatteriesInBatteryPack2 | 1.3.6.1.4.1.44782.1.4.7.2.21 | unsigned integer | r | 0
| batteryPack2BatteryTable | 1.3.6.1.4.1.44782.1.4.7.2.22
| batteryPack2BatteryEntry | 1.3.6.1.4.1.44782.1.4.7.2.22.1
| batteryPack2BatterySerialNumber | 1.3.6.1.4.1.44782.1.4.7.2.22.1.1 | unsigned integer |  | 0 |  | 1~32
| batteryPack2BatteryVoltage | 1.3.6.1.4.1.44782.1.4.7.2.22.1.2 | unsigned integer | r | 2 | V
| batteryPack2BatteryInternalResistance | 1.3.6.1.4.1.44782.1.4.7.2.22.1.3 | unsigned integer | r | 2 | Ω
| batteryPack2BatteryTemperature | 1.3.6.1.4.1.44782.1.4.7.2.22.1.4 | unsigned integer | r | 1 | ℃
| batteryPack2BatterySOC | 1.3.6.1.4.1.44782.1.4.7.2.22.1.5 | unsigned integer | r | 1 | %
| batteryPack2BatterySOH | 1.3.6.1.4.1.44782.1.4.7.2.22.1.6 | unsigned integer | r | 1 | %
| batteryPerformanceOfBatteryPack2 | 1.3.6.1.4.1.44782.1.4.7.2.22.1.7 | unsigned integer | r | - |  | 0 - the battery runs well; 1 - performance degradation; 2 - it is recommended to replace the battery;
| abnormalCommunicationOfBatteryPack2 | 1.3.6.1.4.1.44782.1.4.7.2.22.1.8 | unsigned integer | r | - |  | 0 = normal; 1 = alarm
| batteryPack2BatteryVoltageTooHigh | 1.3.6.1.4.1.44782.1.4.7.2.22.1.9 | unsigned integer | r | - |  | 1 = normal; 1 = alarm
| batteryPack2BatteryVoltageTooLow | 1.3.6.1.4.1.44782.1.4.7.2.22.1.10 | unsigned integer | r | - |  | 2 = normal; 1 = alarm
| batteryPack2BatteryInternalResistanceTooHigh | 1.3.6.1.4.1.44782.1.4.7.2.22.1.11 | unsigned integer | r | - |  | 3 = normal; 1 = alarm
| batteryPack2BatteryTemperatureTooHigh | 1.3.6.1.4.1.44782.1.4.7.2.22.1.12 | unsigned integer | r | - |  | 4 = normal; 1 = alarm
| batteryPack2BatteryTemperatureTooLow | 1.3.6.1.4.1.44782.1.4.7.2.22.1.13 | unsigned integer | r | - |  | 5 = normal; 1 = alarm
| batteryPack2BatteryCapacityTooLow | 1.3.6.1.4.1.44782.1.4.7.2.22.1.14 | unsigned integer | r | - |  | 6 = normal; 1 = alarm
| batteryPack2BatteryOtherFaults | 1.3.6.1.4.1.44782.1.4.7.2.22.1.15 | unsigned integer | r | - |  | 7 = normal; 1 = alarm
Ordinary air conditioner | ac1Name | 1.3.6.1.4.1.44782.1.4.11.1.1 | string | r | -
| ac1CommunicationStatus | 1.3.6.1.4.1.44782.1.4.11.1.2 | unsigned integer | r | -
| ac1Temperature | 1.3.6.1.4.1.44782.1.4.11.1.3 | unsigned integer | r | 1 | ℃
| ac1Humidity | 1.3.6.1.4.1.44782.1.4.11.1.4 | unsigned integer | r | 1 | %
| ac1HighTemperatureStatus | 1.3.6.1.4.1.44782.1.4.11.1.5 | unsigned integer | r | -
| ac1LowTemperatureStatus | 1.3.6.1.4.1.44782.1.4.11.1.6 | unsigned integer | r | -
| ac1HighHumidityStatus | 1.3.6.1.4.1.44782.1.4.11.1.7 | unsigned integer | r | -
| ac1LowHumidityStatus | 1.3.6.1.4.1.44782.1.4.11.1.8 | unsigned integer | r | -
| ac1RunStatus | 1.3.6.1.4.1.44782.1.4.11.1.9 | unsigned integer | r | - |  | 0=stop;1=run
Temperature and humidity module | ths1Name | 1.3.6.1.4.1.44782.1.4.17.1.1 | string | r | -
| ths1CommunicationStatus | 1.3.6.1.4.1.44782.1.4.17.1.2 | unsigned integer | r | -
| ths1Temperature | 1.3.6.1.4.1.44782.1.4.17.1.3 | unsigned integer | r | 1 | ℃
| ths1humidity | 1.3.6.1.4.1.44782.1.4.17.1.4 | unsigned integer | r | 1 | %
| ths1HighTemperatureStatus | 1.3.6.1.4.1.44782.1.4.17.1.5 | unsigned integer | r | -
| ths1LowTemperatureStatus | 1.3.6.1.4.1.44782.1.4.17.1.6 | unsigned integer | r | -
| ths1HighHumidityStatus | 1.3.6.1.4.1.44782.1.4.17.1.7 | unsigned integer | r | -
| ths1LowHumidityStatus | 1.3.6.1.4.1.44782.1.4.17.1.8 | unsigned integer | r | -
| ths1NameOfAuxiliarySwitch1 | 1.3.6.1.4.1.44782.1.4.17.1.9 | unsigned integer | r | -
| ths1AuxiliarySwitch1Status | 1.3.6.1.4.1.44782.1.4.17.1.10 | unsigned integer | r | -
| ths1NameOfAuxiliarySwitch2 | 1.3.6.1.4.1.44782.1.4.17.1.11 | unsigned integer | r | -
| ths1AuxiliarySwitch2Status | 1.3.6.1.4.1.44782.1.4.17.1.12 | unsigned integer | r | -
| ths2Name | 1.3.6.1.4.1.44782.1.4.17.2.1 | string | r | -
| ths2CommunicationStatus | 1.3.6.1.4.1.44782.1.4.17.2.2 | unsigned integer | r | -
| ths2Temperature | 1.3.6.1.4.1.44782.1.4.17.2.3 | unsigned integer | r | 1 | ℃
| ths2humidity | 1.3.6.1.4.1.44782.1.4.17.2.4 | unsigned integer | r | 1 | %
| ths2HighTemperatureStatus | 1.3.6.1.4.1.44782.1.4.17.2.5 | unsigned integer | r | -
| ths2LowTemperatureStatus | 1.3.6.1.4.1.44782.1.4.17.2.6 | unsigned integer | r | -
| thS2HighHumidityStatus | 1.3.6.1.4.1.44782.1.4.17.2.7 | unsigned integer | r | -
| ths2LowHumidityStatus | 1.3.6.1.4.1.44782.1.4.17.2.8 | unsigned integer | r | -
| ths2NameOfAuxiliarySwitch1 | 1.3.6.1.4.1.44782.1.4.17.2.9 | unsigned integer | r | -
| ths2AuxiliarySwitch1Status | 1.3.6.1.4.1.44782.1.4.17.2.10 | unsigned integer | r | -
| ths2NameOfAuxiliarySwitch2 | 1.3.6.1.4.1.44782.1.4.17.2.11 | unsigned integer | r | -
| ths2AuxiliarySwitch2Status | 1.3.6.1.4.1.44782.1.4.17.2.12 | unsigned integer | r | -
| ths3Name | 1.3.6.1.4.1.44782.1.4.17.3.1 | string | r | -
| ths3CommunicationStatus | 1.3.6.1.4.1.44782.1.4.17.3.2 | unsigned integer | r | -
| ths3Temperature | 1.3.6.1.4.1.44782.1.4.17.3.3 | unsigned integer | r | 1 | ℃
| ths3humidity | 1.3.6.1.4.1.44782.1.4.17.3.4 | unsigned integer | r | 1 | %
| ths3HighTemperatureStatus | 1.3.6.1.4.1.44782.1.4.17.3.5 | unsigned integer | r | -
| ths3LowTemperatureStatus | 1.3.6.1.4.1.44782.1.4.17.3.6 | unsigned integer | r | -
| thS3HighHumidityStatus | 1.3.6.1.4.1.44782.1.4.17.3.7 | unsigned integer | r | -
| ths3LowHumidityStatus | 1.3.6.1.4.1.44782.1.4.17.3.8 | unsigned integer | r | -
| ths3NameOfAuxiliarySwitch1 | 1.3.6.1.4.1.44782.1.4.17.3.9 | unsigned integer | r | -
| ths3AuxiliarySwitch1Status | 1.3.6.1.4.1.44782.1.4.17.3.10 | unsigned integer | r | -
| ths3NameOfAuxiliarySwitch2 | 1.3.6.1.4.1.44782.1.4.17.3.11 | unsigned integer | r | -
| ths3AuxiliarySwitch2Status | 1.3.6.1.4.1.44782.1.4.17.3.12 | unsigned integer | r | -
| ths4Name | 1.3.6.1.4.1.44782.1.4.17.4.1 | string | r | -
| ths4CommunicationStatus | 1.3.6.1.4.1.44782.1.4.17.4.2 | unsigned integer | r | -
| ths4Temperature | 1.3.6.1.4.1.44782.1.4.17.4.3 | unsigned integer | r | 1 | ℃
| ths4humidity | 1.3.6.1.4.1.44782.1.4.17.4.4 | unsigned integer | r | 1 | %
| ths4HighTemperatureStatus | 1.3.6.1.4.1.44782.1.4.17.4.5 | unsigned integer | r | -
| ths4LowTemperatureStatus | 1.3.6.1.4.1.44782.1.4.17.4.6 | unsigned integer | r | -
| thS4HighHumidityStatus | 1.3.6.1.4.1.44782.1.4.17.4.7 | unsigned integer | r | -
| ths4LowHumidityStatus | 1.3.6.1.4.1.44782.1.4.17.4.8 | unsigned integer | r | -
| ths4NameOfAuxiliarySwitch1 | 1.3.6.1.4.1.44782.1.4.17.4.9 | string | r | -
| ths4AuxiliarySwitch1Status | 1.3.6.1.4.1.44782.1.4.17.4.10 | unsigned integer | r | -
| ths4NameOfAuxiliarySwitch2 | 1.3.6.1.4.1.44782.1.4.17.4.11 | string | r | -
| ths4AuxiliarySwitch2Status | 1.3.6.1.4.1.44782.1.4.17.4.12 | unsigned integer | r | -
Distribution switch | pdcStwitch1Name | 1.3.6.1.4.1.44782.1.4.19.1.1 | string | r | -
| pdcStwitch1CommunicationStatus | 1.3.6.1.4.1.44782.1.4.19.1.2 | unsigned integer | r | -
| pdcStwitch1ACBreaker1Status | 1.3.6.1.4.1.44782.1.4.19.1.3 | unsigned integer | r | -
| pdcStwitch1ACBreaker2Status | 1.3.6.1.4.1.44782.1.4.19.1.4 | unsigned integer | r | -
| pdcStwitch1ACBreaker3Status | 1.3.6.1.4.1.44782.1.4.19.1.5 | unsigned integer | r | -
| pdcStwitch1ACBreaker4Status | 1.3.6.1.4.1.44782.1.4.19.1.6 | unsigned integer | r | -
| pdcStwitch1ACBreaker5Status | 1.3.6.1.4.1.44782.1.4.19.1.7 | unsigned integer | r | -
| pdcStwitch1ACBreaker6Status | 1.3.6.1.4.1.44782.1.4.19.1.8 | unsigned integer | r | -
| pdcStwitch1ACBreaker7Status | 1.3.6.1.4.1.44782.1.4.19.1.9 | unsigned integer | r | -
| pdcStwitch1ACBreaker8Status | 1.3.6.1.4.1.44782.1.4.19.1.10 | unsigned integer | r | -
Switching value module | SwitchModule1Name | 1.3.6.1.4.1.44782.1.4.20.1.1 | string | r | -
| SwitchModule1CommunicationStatus | 1.3.6.1.4.1.44782.1.4.20.1.2 | unsigned integer | r | -
| SwitchModule1DryContactNumber | 1.3.6.1.4.1.44782.1.4.20.1.3 | unsigned integer | r | 0
| SwitchModule1DryContactTable | 1.3.6.1.4.1.44782.1.4.20.1.4
| SwitchModule1DryContactEntry | 1.3.6.1.4.1.44782.1.4.20.1.4.1
| SwitchModule1DryContactIndex | 1.3.6.1.4.1.44782.1.4.20.1.4.1.1.1 | unsigned integer | r | -
| SwitchModule1DryContactName | 1.3.6.1.4.1.44782.1.4.20.1.4.1.2.1 | unsigned integer | r | -
| SwitchModule1DryContactStatus | 1.3.6.1.4.1.44782.1.4.20.1.4.1.3.1 | unsigned integer | r | -